## Slide 1
Water Circulation Guide
If the pump is making noise, check the priming. If the noise persists replace the mechanical seal.
Inlet completely filled with water?
Prime the pump
Yes
No
Turn the pump on
Water flowing through outlet?
Can turn the chiller on
Start
Yes
No
Starting the Water Circulation:

## Slide 2
Water Circulation Guide
It is important to turn the chiller off if there is no water circulation to prevent the damage to the chiller.
Is the chiller on?
Yes
No
Turn the chiller off
Turn the pump off
Start
Stopping the Water Circulation:

## Slide 3
Pump Priming Guide
Open both inlet and outlet ports by removing the plug.
2. Fill the outlet port with water (as shown in Fig 2) until the inlet line and the pump body are completely filled with water.
You may need to shake the inlet line to help trapped air escape.
It is important to have both port open to allow the air from the inlet and pump body to escape.
Inlet plug
Outlet plug
3. Close both inlet and outlet ports.
If properly primed, the unit should start pumping immediately. If not repeat the priming procedure.
Fig 1: Red Lion RJSE-75SS pump
Fig 2: Priming the pump